## Inputs
name | value | unit | description
r | 0.085 | per year | Discount rate (CDRI 8.5%)
growth | 0 | per decade | Wind-speed growth (climate)
cost | 0.73047 | INR cr/tower | Repair cost per damaged tower (Fani DLNA)
days | 7 | days | Outage duration
kwh | 3 | kWh/person/day | Energy served per person
voll | 100 | INR/kWh | Value of lost load
renewal | 0.03 | share/yr | (a) towers built/rebuilt per year
new_cost | 0.6 | INR cr/tower | (a) new tower cost
incr | 0.2 | share | (a) extra cost of higher design
n_a | 9672 | towers | (a) towers in coastal band
retrofit | 0.35 | INR cr/tower | (b) retrofit cost
build | 3 | years | (b) build period
n_b | 3590 | towers | (b) towers on top lines

## EAD
option | towers_at_scale1 | towers_slope | pop_at_scale1 | pop_slope | note
base | 93.4132 | 392.2781 | 474217.3943 | 1644585.8104 | expected damaged towers / person-outages per year (from Notebook 06 risk runs)
a | 57.8255 | 287.0694 | 323884.2679 | 1218628.8238 | expected damaged towers / person-outages per year (from Notebook 06 risk runs)
b | 78.6898 | 344.5115 | 439896.5849 | 1568852.6892 | expected damaged towers / person-outages per year (from Notebook 06 risk runs)

## CashFlows
year | discount_factor | hazard_scale | share_a_built | share_b_built | EAD_base | EAD_a_full | EAD_b_full | EAD_a | EAD_b | cost_a | cost_b | benefit_a | benefit_b | PV_benefit_a | PV_cost_a | PV_benefit_b | PV_cost_b
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30

## Results
option | PV benefits (cr) | PV costs (cr) | NPV (cr) | BCR
(a) raise design wind, new lines
(b) harden top corridors
(c) do nothing | 0 | 0 | 0
Python check (same inputs): | 0.49218 | 0.16539 | BCR (a), BCR (b)

## Tornado
option | input | low_value | high_value | bcr_low | bcr_high | bcr_base | swing
a | Discount rate | 0.1 | 0.06 | 0.45512 | 0.56255 | 0.49218 | 0.10743
b | Discount rate | 0.1 | 0.06 | 0.14737 | 0.206 | 0.16539 | 0.058629
a | Value of lost load (INR/kWh) | 40 | 250 | 0.33023 | 0.89706 | 0.49218 | 0.56683
b | Value of lost load (INR/kWh) | 40 | 250 | 0.12557 | 0.26493 | 0.16539 | 0.13936
a | Outage days | 3 | 14 | 0.33794 | 0.7621 | 0.49218 | 0.42416
b | Outage days | 3 | 14 | 0.12747 | 0.23175 | 0.16539 | 0.10428
a | kWh per person per day | 1.5 | 4.5 | 0.35722 | 0.62714 | 0.49218 | 0.26992
b | kWh per person per day | 1.5 | 4.5 | 0.13221 | 0.19857 | 0.16539 | 0.066361
a | Repair cost per tower (cr) | 0.5 | 1 | 0.42205 | 0.57419 | 0.49218 | 0.15214
b | Repair cost per tower (cr) | 0.5 | 1 | 0.13414 | 0.20193 | 0.16539 | 0.067782
a | Climate: wind growth per decade | 0 | 0.04 | 0.49218 | 0.58257 | 0.49218 | 0.090387
b | Climate: wind growth per decade | 0 | 0.04 | 0.16539 | 0.18551 | 0.16539 | 0.020127
a | (a) incremental cost % | 0.4 | 0.1 | 0.24609 | 0.98436 | 0.49218 | 0.73827
b | (a) incremental cost % | 0.4 | 0.1 | 0.16539 | 0.16539 | 0.16539 | 0
a | (a) renewal rate | 0.02 | 0.05 | 0.49218 | 0.52641 | 0.49218 | 0.034233
b | (a) renewal rate | 0.02 | 0.05 | 0.16539 | 0.16539 | 0.16539 | 0
a | (a) capacity gain | a_lo | a_hi | 0.29631 | 0.62466 | 0.49218 | 0.32835
b | (a) capacity gain | a_lo | a_hi | 0.16539 | 0.16539 | 0.16539 | 0
a | (b) retrofit cost per tower (cr) | 0.5 | 0.25 | 0.49218 | 0.49218 | 0.49218 | 0
b | (b) retrofit cost per tower (cr) | 0.5 | 0.25 | 0.11577 | 0.23154 | 0.16539 | 0.11577
a | (b) capacity gain | b_lo | b_hi | 0.49218 | 0.49218 | 0.49218 | 0
b | (b) capacity gain | b_lo | b_hi | 0.1225 | 0.20101 | 0.16539 | 0.078503